## Slide 1
AeroBarrier Technology Development
Mark Modera
UC Davis and Aeroseal
August 4, 2025

## Slide 2: Presentation Overview
Conceptualization of Envelope Sealing Process
  Seal Rate Analysis
  Transport Efficiency
  Sealing Simulation Tool
Dedicated Test Facility
  Sealing Rate Comparison
  Separation of Effects Impacting Seal Rate
New Technology Developments
  Smaller, Lighter, Faster System
  Non-Electric Heat
  Airless Atomization
New Applications
  Ceiling Plenum Sealing
  Underfloor Sealing

## Slide 3: Envelope Sealing Process
Pressurize Building with a Fan
  Blower Door on Steroids
Inject Aerosolized Sealant
  Air carries sealant to Leaks
Track Sealing Process
  Feedback to Technician
  Documentation for Builder (or homeowner)

## Slide 4: Conceptualization of Envelope Sealing Process
Seal Rate Analysis
where:
InjRate is max sealant injection (limited by psychrometrics)
htrans is Transport Efficiency (fraction getting to leaks)
hdep is Deposition Efficiency (fraction depositing in leaks)
SealDensity is sealant required to seal a given size leak

## Slide 5: Conceptualization of Envelope Sealing Process
Transport Efficiency
Settling Velocity
Floor Area

## Slide 6: Conceptualization of Envelope Sealing Process
Transport Efficiency
Basically a race between getting to the leaks before falling to the floor
where:
Vsettling is Settling Velocity (like terminal velocity), a strong function of
particle size

## Slide 7: Conceptualization of Envelope Sealing Process
Sealing Simulation Tool
Aerobarrier Sealing Performance Model - 071225present.xlsm

## Slide 8: Conceptualization of Envelope Sealing Process
Sealing Simulation Tool
Aerobarrier Sealing Performance Model - 071225present.xlsm

## Slide 9: Dedicated Test Facility

## Slide 10: Dedicated Test Facility

## Slide 11: Dedicated Test Facility

## Slide 12: Dedicated Test Facility
Uses concentration measurement boxes to determine Transport Efficiency at FOUR different locations

## Slide 13: Dedicated Test Facility
Uses re-usable leakage plates to assure the same conditions for all tests

## Slide 14: Dedicated Test Facility
  Facilitates calculation of sealant use efficiency
  Facilitates calculation of Deposition Efficiency
Uses scale to weigh plates before and after sealing to determine SealDensity
Uses 2nd scale to weigh total sealant injected

## Slide 15: New Technology Developments
  Non-Electric Heat =
  Smaller, Lighter, Faster System
  220 V Fan
  Large heavy Compressor/Generator
  Compressed Air lines running into house
  Non-Electric Heat
  110 V Fan
  35% less weight

## Slide 16: New Technology Developments
  Non-Electric Heat + Airless Atomization =
  Smaller, Lighter, Faster System
  Airless Atomization - No Compressed Air
  Battery-powered sealing stations
  Another 50% weight and volume reduction
  Non-Electric Heat
  110 V Fan
  35% less weight

## Slide 17: Dedicated Test Facility Application
Quantifying Transport Efficiency
Chart: Transport Efficiency
| C1 (north) | C2 (middle) | C3 (south) | C4 (south- low) | North/South | High/Low
Worst | 0.16688 | 0.26534 | 0.17917 | 0.38676 | 0.9314 | 0.46325
Average | 0.34536 | 0.55464 | 0.37563 | 0.54047 | 0.91942 | 0.69501
Best | 0.71 | 0.97 | 0.62 | 0.63 | 1.1452 | 0.98413

## Slide 18: Dedicated Test Facility Application
Getting Airless sealing speeds to match Compressor Systems
Compressor
Airless
New Airless
Compressor
Compressor
Airless

## Slide 19: Field Testing Airless System
Saves 20 mins on set-up and clean-up
Has had longer injection times versus Compressed Air
Last week AIRLESS showed shorter injection times versus Compressed Air, based upon innovations tested in the lab

## Slide 20: New Applications
Ceiling Plenum Sealing
  PROTOCOL
  Preparation
    Applied spray foam to patch large existing openings between ceiling plenum and adjacent ceiling plenum (i.e. gaps in corrugated roof deck)
    Positioned 3 mobile sealant injection stations in the ceiling plenum nearest the perimeter walls
    Opened ceiling tiles furthest from the sealing stations to ensure air penetration from the blower door into the ceiling plenum
  Injection performed during normal operating hours in an occupied office building
    Used an additional blower door to pressurize an adjacent room to limit sealant infiltration into the rest of the facility

## Slide 21: New Applications
  Results
    Sealed approximately 300 cfm50
    Stopped prematurely due to some fogging of occupied space
    Should be performed during unoccupied hours
      Not enough fogging to cause deposition, but enough to cause complaints
Ceiling Plenum Sealing

## Slide 22: New Applications
Underfloor Air Distribution Sealing
Parameter | Value
Envelope Height (H1) | 9.9 ft
Subfloor Height (H2) | 1 ft
Envelope Width (W) | 18.2 ft
Envelope Length (L) | 31.3 ft
Envelope Volume (L x W x H1) | 5,630 cubic feet

## Slide 23: New Applications
Underfloor Air Distribution Sealing
Parameter | Value
Envelope Pre-seal Leakage | 6.3 ACH50
Envelope Post-seal Leakage | 4.9 ACH50
Subfloor Initial Leakage | 747 CFM25
Subfloor Final Leakage | 75 CFM25

## Slide 24: Presentation Take-Aways
Facility for Precise Measurement of Aerosol Envelope Sealing Technologies
  Separates out factors influencing performance
Airless Envelope Sealing is the Future
  Surpassed current Air-Assist atomization in lab and field
  Dramatically reduces equipment weight and volume
  Reduces set-up and break-down time requirements
New Applications
  Continue to find new applications for the technology